## Slide 1: Line Limit Preserving Power System Equivalent
Wonhyeok Jang
Work with Prof. Overbye, Saurav Mohapatra & Hao Zhu
ECE 590I

## Slide 2: Contents
Introduction
Preliminaries
Cases
Algorithm
Examples
Conclusions

## Slide 3: Introduction
Equivalent power system
  A model system with fewer nodes and branches than the original
Purpose of equivalent
  More efficient simulation
  Without sacrificing too much fidelity of simulation results of the original

## Slide 4: Introduction
Ward equivalent (Kron’s reduction)
  Traditional method to equivalence power system network models
  Loses desired attributes of the original system
Objective of work
  Develop equivalents that preserve desired attributes, the line limits in this work, of the original system

## Slide 5: Preliminary – Line limits
Thermal line limits are intended to limit
  Temperature attained by the energized conductors
  Resulting sag
  Loss of tensile strength
Limits are calculated where conductor sag is at minimum allowable clearance
  Geographical condition
  Climate condition

## Slide 6: Preliminary - Kron’s reduction
When a bus k between bus i and j is equivalenced
  First term on RHS is admittance of existing line
  Second term on RHS is admittance of equivalent line
Theses equivalent lines have no limits
Goal is to assign limits to theses equivalent lines that preserve desired attribute of the original

## Slide 7: Preliminary - PTDF
Power Transfer Distribution Factor
  Linear approximation of the impact of power flowing on each line w.r.t the amount t of an arbitrary basic transaction w
    ∆fl: fraction of power transfer flowing on line l
    ∆t: specific amount of transaction w
    Basic transaction

## Slide 8: Preliminary - PTDF
PTDFs on the retained lines are not affected by equivalencing
Original system with PTDFs from 2 to 3
Equivalent system with PTDFs from 2 to 3

## Slide 9: Preliminary - MPT
Desired attribute to preserve by assigning limits
  Maximum power transfer (MPT) between retained buses match that for the same buses in the original
MPT between bus i and j can be calculated with PTDF
    l: each line of the system
Need to match for MPTs between all the first neighbor buses of the bus being eliminated

## Slide 10: General Case
Bus E, between bus A and B, is going to be eliminated
Need to calculate the new limit for the equivalent line between bus A and B

## Slide 11: Special Case
Series Combination
  If two lines are in series and the node joining them is equivalenced, then the total limit must be the lower of the two limits

## Slide 12: Special Case
Parallel Combination
  New limit is determined by which line in the parallel lines is binding

## Slide 13: Algorithm
Sequentially as each bus is being equivalenced
  Combine limits of parallel lines
  Calculate PTDFs between the first neighbor buses
  Calculate MPT between the first neighbor buses, only considering the lines that are being eliminated
    Limits on the retained lines do not need to be considered since they remain the same
  Determine limits for equivalent lines so the MPTs of the equivalent match that in the original

## Slide 14: Ex - 4 bus system
MPTs in the original system
  MPT 2-3: 216.7 MW (1-3 binding)
  MPT 2-4: 171.7 MW (1-4 binding)
  MPT 3-4: 144.9 MW (1-4 binding)
For 2-3 direction, eq. line limits are
  Lim23 >= 216.7*0.234 = 50.7 MW
  Lim24 >= 216.7*0.024 = 5.2 MW
  Lim34 >= 216.7*0.088 = 19.1 MW
Original system with PTDF from 2 to 3
Reduced system with PTDF from 2 to 3

## Slide 15: Ex - 4 bus system (Exact solution)
 | Directions |  | 
 | 2-3 | 2-4 | 3-4
Eq Lim 23 >= | 50.7 MW | 4.8 MW | 29.8 MW
Eq Lim 24 >= | 5.2 MW | 41.4 MW | 31.4 MW
Eq Lim 34 >= | 19.1 MW | 18.7 MW | 28.5 MW
  Often, solution is just the largest in each row
  This works when each column has one solution
  There are cases with no exact solutions when equality constraints for at least one direction may not by satisfied

## Slide 16: Ex - 4 bus system (No solution 1 - Overestimate)
When there’s no solution -> Bound the solution
Line limit 1-4 is reduced from 60 MVA to 20 MVA
  Others are all the same with the original
MPTs in the original system
  MPT 2-3: 216.7 MW (1-3 binding)
  MPT 2-4: 57.2 MW (1-4 binding)
  MPT 3-4: 48.3 MW (1-4 binding)
Original system with PTDF from 2 to 3

## Slide 17: Ex - 4 bus system (No solution 1 - Overestimate)
All of the inequality constraints are satisfied for each row
But power flow in direction 3-4 is overestimated since no entries in its column is enforced
 | Directions |  | 
 | 2-3 | 2-4 | 3-4
Eq Lim 23 >= | 50.7 MW | 1.6 MW | 9.9 MW
Eq Lim 24 >= | 5.2 MW | 13.8 MW | 10.5 MW
Eq Lim 34 >= | 19.1 MW | 6.2 MW | 9.5 MW

## Slide 18: Ex - 4 bus system (No solution 2 - underestimate)
We make sure power flow in each direction is less than the original MPT
Then at least one inequality constraints would be violated and this will underestimate the MPT
We define “limit violation cost” for each entry of the matrix, which is the sum of violations for all entries in each row

## Slide 19: Ex - 4 bus system (No solution 2 - underestimate)
For the first row, the 2-3 entry is 0 since it involves no limit violations;
the 2-4 entry 57.4 = (50.7 – 1.6) + (9.9 – 1.6)
The 3-4 entry 40.8 = (50.7 – 9.9)
 | Directions |  | 
 | 2-3 | 2-4 | 3-4
Eq Lim 23 >= | 50.7 MW | 1.6 MW | 9.9 MW
Eq Lim 24 >= | 5.2 MW | 13.8 MW | 10.5 MW
Eq Lim 34 >= | 19.1 MW | 6.2 MW | 9.5 MW
 | Directions |  | 
 | 2-3 | 2-4 | 3-4
Eq Lim 23 | 0 | 57.4 | 40.8
Eq Lim 24 | 13.9 | 0 | 3.3
Eq Lim 34 | 0 | 16.2 | 9.6
Limit violation cost matrix
Original eq. line limit matrix

## Slide 20: Ex - 4 bus system (No solution 2 - underestimate)
Minimum matching problem – Hungarian algorithm
  Choose one entry in each row and each column that minimizes the sum of the violation costs
 | Directions |  | 
 | 2-3 | 2-4 | 3-4
Eq Lim 23 | 0 | 57.4 | 40.8
Eq Lim 24 | 13.9 | 0 | 3.3
Eq Lim 34 | 0 | 16.2 | 9.6
Limit violation cost matrix
 | Directions |  | 
 | 2-3 | 2-4 | 3-4
Eq Lim 23 >= | 50.7 MW | 1.6 MW | 9.9 MW
Eq Lim 24 >= | 5.2 MW | 13.8 MW | 10.5 MW
Eq Lim 34 >= | 19.1 MW | 6.2 MW | 9.5 MW
Underestimate solution

## Slide 21: Conclusions
Able to determine limits for eq. lines
In case of no exact limits, we bound the limits
When the number of first neighbor buses increase, then there’s rapid increase of the number of computation
There’s a certain value of line limits that turns a exact solution case to no exact solution case
Investigation of which factor changes solution types is needed

## Slide 22
Thank you!

## Slide 23: Ex - 7 bus system
Original 7-bus system
Eliminating bus 3

## Slide 24: Ex - 7 bus system
 | 1-2 | 1-4 | 2-4
Eqv Line 1-2 | 11.2 MW | 4.1 MW | 1.2 MW
Eqv Line 1-4 | 53.8 MW | 56.8 MW | 38.7 MW
Eqv Line 2-4 | 17.8 MW | 43.2 MW | 61.3 MW
Determination of equivalent line limits
MPT comparison of all lines between 7-bus and 6-bus
 | 1-2 | 1-4 | 2-4
Original 7-bus | 118.7 MW (line 1-2 binding) | 148.2 MW (line 1-2 binding) | 223.7 MW (line 3-4 binding)
Reduced 6-bus | 118.7 MW (line 1-2 binding) | 148.2 MW (line 1-2 binding) | 223.7 MW (Eq line 2-4 binding)
Error rate (%) | 0.0 | 0.0 | 0.0
MPT comparison of lines being eliminated between 7-bus and 6-bus
 | 1-2 | 1-4 | 2-4
Original 7-bus | 412.1 MW (line 1-3 binding) | 187.1 MW (line 3-4 binding) | 223.7 MW (line 3-4 binding)
Reduced 6-bus | 412.1 MW (Eq line 1-2 binding) | 187.1 MW (Eq line 1-4 binding) | 223.7 MW (Eq line 2-4 binding)
Error rate (%) | 0.0 | 0.0 | 0.0

## Slide 25: Ex - 7 bus system
Equivalent 6-bus system
Eliminating bus 5

## Slide 26: Ex - 7 bus system
 | 2-4 | 2-7 | 4-7
Eqv Line 2-4 | 22.9 MW | 3.6 MW | 10.6 MW
Eqv Line 2-7 | 17.1 MW | 96.4 MW | 56.5 MW
Eqv Line 4-7 | 37.1 MW | 41.1 MW | 49.4 MW
Determination of equivalent line limits
MPT comparison of all lines between 6-bus and 5-bus
 | 2-4 | 2-7 | 4-7
Reduced 6-bus | 223.7 MW (line 2-4 binding) | 250.1 MW (line 2-5 binding) | 171.8 MW (line 4-5 binding)
Reduced 5-bus | 223.7 MW (line 2-4 binding) | 250.1 MW (Eq line 2-7 binding) | 171.8 MW (Eq line 4-7 binding)
Error rate (%) | 0.0 | 0.0 | 0.0
MPT comparison of lines being eliminated between 6-bus and 5-bus
 | 2-4 | 2-7 | 4-7
Reduced 6-bus | 301.4 MW (line 4-5 binding) | 250.1 MW (line 2-5 binding) | 171.8 MW (line 4-5 binding)
Reduced 5-bus | 301.4 MW (Eq line 2-4 binding) | 250.1 MW (Eq line 2-7 binding) | 171.8 MW (Eq line 4-7 binding)
Error rate (%) | 0.0 | 0.0 | 0.0

## Slide 27: Ex - 7 bus system
Equivalent 5-bus system
Eliminating bus 2

## Slide 28: Ex - 7 bus system (overestimate)
 | 1-4 | 1-6 | 1-7 | 4-6 | 4-7 | 6-7
Eqv Line 1-4 | 53.4 MW | 20.2 MW | 23.8 MW | 0.1 MW | 45.9 MW | 9.6 MW
Eqv Line 1-6 | 37.5 MW | 68.2 MW | 53.4 MW | 75.0 MW | 49.6 MW | 50.4 MW
Eqv Line 1-7 | 12.4 MW | 14.9 MW | 26.0 MW | 9.6 MW | 35.1 MW | 32.6 MW
Eqv Line 4-6 | 27.6 MW | 24.3 MW | 11.2 MW | 92.6 MW | 76.3 MW | 41.7 MW
Eqv Line 4-7 | 6.8 MW | 4.0 MW | 10.1 MW | 18.9 MW | 35.2 MW | 18.3 MW
Eqv Line 6-7 | 1.6 MW | 4.5 MW | 10.4 MW | 11.4 MW | 20.2 MW | 45.5 MW
Determination of equivalent line limits

## Slide 29: Ex - 7 bus system (overestimate)
MPT comparison of all lines between 5-bus and 4-bus
 | 1-4 | 1-6 | 1-7 | 4-6 | 4-7 | 6-7
Reduced 5-bus | 148.2 MW (line 1-2 binding) | 120.2 MW (line 1-2 binding) | 123.3 MW (line 1-2 binding) | 238.6 MW (line 2-4 binding) | 171.8 MW (line 4-7 binding) | 375.1 MW (line 2-7 binding)
Reduced 4-bus | 148.2 MW (Eq line 1-4 binding) | 132.2 MW (Eq line 1-6 binding) | 154.9 MW (Eq line 1-7 binding) | 238.6 MW (Eq line 1-6 binding) | 171.8 MW (line 4-7 binding) | 375.1 MW (Eq line 6-7 binding)
Error rate (%) | 0.0 | 10.0 | 34.9 | 0.0 | 0.0 | 0.0
MPT comparison of lines being eliminated between 5-bus and 4-bus
 | 1-4 | 1-6 | 1-7 | 4-6 | 4-7 | 6-7
Reduced 5-bus | 148.2 MW (line 1-2 binding) | 120.2 MW (line 1-2 binding) | 123.3 MW (line 1-2 binding) | 238.6 MW (line 2-4 binding) | 275.3 MW (line 2-4 binding) | 375.1 MW (line 2-7 binding)
Reduced 4-bus | 148.2 MW (Eq line 1-4 binding) | 132.2 MW (Eq line 1-6 binding) | 166.4 MW (Eq line 1-7 binding) | 238.6 MW (Eq line 1-6 binding) | 275.3 MW (Eq line 1-7 & Eq line 4-7 binding) | 375.1 MW (Eq line 6-7 binding)
Error rate (%) | 0.0 | 10.0 | 34.9 | 0.0 | 0.0 | 0.0

## Slide 30: Ex - 7 bus system (underestimate)
 | 1-4 | 1-6 | 1-7 | 4-6 | 4-7 | 6-7
Eqv Line 1-4 | 53.4 MW | 20.2 MW | 23.8 MW | 0.1 MW | 45.9 MW | 9.6 MW
Eqv Line 1-6 | 37.5 MW | 68.2 MW | 53.4 MW | 75.0 MW | 49.6 MW | 50.4 MW
Eqv Line 1-7 | 12.4 MW | 14.9 MW | 26.0 MW | 9.6 MW | 35.1 MW | 32.6 MW
Eqv Line 4-6 | 27.6 MW | 24.3 MW | 11.2 MW | 92.6 MW | 76.3 MW | 41.7 MW
Eqv Line 4-7 | 6.8 MW | 4.0 MW | 10.1 MW | 18.9 MW | 35.2 MW | 18.3 MW
Eqv Line 6-7 | 1.6 MW | 4.5 MW | 10.4 MW | 11.4 MW | 20.2 MW | 45.5 MW
Determination of equivalent line limits
 | 1-4 | 1-6 | 1-7 | 4-6 | 4-7 | 6-7
Eqv Line 1-4 | 0.0 | 62.7 | 51.6 | 152.3 | 7.5 | 104.8
Eqv Line 1-6 | 96.9 | 6.8 | 36.4 | 0.0 | 36.6 | 45.5
Eqv Line 1-7 | 59.1 | 49.0 | 15.7 | 72.7 | 0.0 | 2.4
Eqv Line 4-6 | 127.7 | 141.2 | 206.5 | 0.0 | 16.3 | 85.6
Eqv Line 4-7 | 55.1 | 69.5 | 42.1 | 16.3 | 0.0 | 17.5
Eqv Line 6-7 | 84.1 | 69.7 | 46.0 | 42.9 | 25.3 | 0.0
Limit violation costs

## Slide 31: Ex - 7 bus system (underestimate)
Find minimum sum of limit violation costs using Hungarian algorithm
 | 1-4 | 1-6 | 1-7 | 4-6 | 4-7 | 6-7 | 
Eqv Line 1-4 | 0.00 | 55.86 | 35.88 | 152.28 | 7.47 | 104.80 | 0
Eqv Line 1-6 | 96.94 | 0.00 | 20.66 | 0.00 | 36.63 | 45.51 | 0
Eqv Line 1-7 | 59.12 | 42.26 | 0.00 | 72.73 | 0.00 | 2.44 | 0
Eqv Line 4-6 | 127.69 | 134.38 | 190.79 | 0.00 | 16.33 | 85.61 | 0
Eqv Line 4-7 | 55.11 | 62.68 | 26.42 | 16.33 | 0.00 | 17.54 | 0
Eqv Line 6-7 | 84.13 | 62.94 | 30.32 | 42.94 | 25.29 | 0.00 | 0
 | 0 | 6.79 | 15.72 | 0 | 0 | 0 | 22.51

## Slide 32: Ex - 7 bus system (underestimate)
Find minimum sum of limit violation costs using Hungarian algorithm
 | 1-4 | 1-6 | 1-7 | 4-6 | 4-7 | 6-7 | 
Eqv Line 1-4 | 0.00 | 55.86 | 35.88 | 152.28 | 7.47 | 104.80 | 0
Eqv Line 1-6 | 96.94 | 0.00 | 20.66 | 0.00 | 36.63 | 45.51 | 0
Eqv Line 1-7 | 59.12 | 42.26 | 0.00 | 72.73 | 0.00 | 2.44 | 0
Eqv Line 4-6 | 127.69 | 134.38 | 190.79 | 0.00 | 16.33 | 85.61 | 0
Eqv Line 4-7 | 55.11 | 62.68 | 26.42 | 16.33 | 0.00 | 17.54 | 0
Eqv Line 6-7 | 84.13 | 62.94 | 30.32 | 42.94 | 25.29 | 0.00 | 0
 | 0 | 6.79 | 15.72 | 0 | 0 | 0 | 22.51

## Slide 33: Ex - 7 bus system (underestimate)
Determination of equivalent line limits
 | 1-4 | 1-6 | 1-7 | 4-6 | 4-7 | 6-7
Eqv Line 1-4 | 53.4 | 20.2 | 23.8 | 0.1 | 45.9 | 9.6
Eqv Line 1-6 | 37.5 | 68.2 | 53.4 | 75.0 | 49.6 | 50.4
Eqv Line 1-7 | 12.4 | 14.9 | 26.0 | 9.6 | 35.1 | 32.6
Eqv Line 4-6 | 27.6 | 24.3 | 11.2 | 92.6 | 76.3 | 41.7
Eqv Line 4-7 | 6.8 | 4.0 | 10.1 | 18.9 | 35.2 | 18.3
Eqv Line 6-7 | 1.6 | 4.5 | 10.4 | 11.4 | 20.2 | 45.5

## Slide 34: Ex - 7 bus system (underestimate)
MPT comparison of all lines between 5-bus and 4-bus
 | 1-4 | 1-6 | 1-7 | 4-6 | 4-7 | 6-7
Reduced 5-bus | 148.2 MW (line 1-4 binding) | 120.2 MW (line 1-2 binding) | 123.3 MW (line 1-2 binding) | 238.6 MW (line 2-4 binding) | 171.8 MW (line 4-7 binding) | 375.1 MW (line 2-7 binding)
Reduced 4-bus | 148.2 MW (line 1-4 binding) | 120.2 MW (Eq line 1-6 binding) | 123.3 MW (Eq line 1-7 binding) | 217.0 MW (Eq line 1-6 binding) | 171.8 MW (line 4-7 binding) | 298.7 MW (Eq line 1-7 binding)
Error rate (%) | 0.0 | 0.0 | 0.0 | -9.1 | 0.0 | -20.4
MPT comparison of lines being eliminated between 5-bus and 4-bus
 | 1-4 | 1-6 | 1-7 | 4-6 | 4-7 | 6-7
Reduced 5-bus | 148.2 MW (line 1-2 binding) | 120.2 MW (line 1-2 binding) | 123.3 MW (line 1-2 binding) | 238.6 MW (line 2-4 binding) | 275.3 MW (line 2-4 binding) | 375.1 MW (line 2-7 binding)
Reduced 4-bus | 148.2 MW (Eq line 1-4 binding) | 120.2 MW (Eq line 1-6 binding) | 123.3 MW (Eq line 1-7 binding) | 217.0 MW (Eq line 1-6 binding) | 204.0 MW (Eq line 1-7 binding) | 298.7 MW (Eq line 1-7 binding)
Error rate (%) | 0.0 | 0.0 | 0.0 | -9.1 | -25.9 | -20.4