## Slide 1: Power Electronic Drivers’ Influence on LED Light Flicker
Brad Lehman
Northeastern University
lehman@ece.neu.edu
Collaborators: Arnold Wilkins, University of Essex; Anindita Bhattacharya; Semtech, Dustin Rand, Northern Power; Jennifer Veitch, NRC of Canada, Anatoly Shteynberg, Dialog Semiconductor; Michael Poplawski and Naomi Miller, PNNL

## Slide 2: Disclaimer
The views and opinions of this presentation do not represent views of the IEEE or IEEE PAR 1789 working group, but only reflect opinions of the presenter

## Slide 3: Presentation outline
Introduction LED Lighting
Flicker in Lighting
LED drivers and flicker
Conclusions

## Slide 4: Introduction to LED Lighting
Source: US Green Building Council, Massachusetts chapter (June 2013)
http://usgbcma.blogspot.com/2013/06/say-goodbye-to-incandescent-lamp-and.html

## Slide 5
Applications of HB-LEDs
Illumination
-- Local Illumination
-- General Lighting
Ref : www.lumileds.com
www.colorkinetics.com

## Slide 6
Motivation
People LOVE light quality from LEDs!
Brad Lehman lit by CFL
Brad lit by incandescent
Brad lit by LEDs
Notes: 6

## Slide 7
Why High Brightness LEDs?
LEDs have an incredibly long life, lasting ~50,000 hours (depends on operating temperature). A fluorescent tube lasts 7,500 hours and a normal incandescent bulb lasts only 1,000 hours.
LED bulbs are environmentally friendly and no mercury to dispose of
as in some fluorescent lamps.
Lumileds
Nichia
Cree
Enlux
Lower maintenance cost as LEDs have long lifetimes. For the same
reason replacement costs are also reduced.
High-levels of brightness and intensity as combinations of Red, Green
and Blue produce various colors.
Can be easily controlled and programmed.

## Slide 8
Predictions
According to statistics published by Optoelectronics Industry Development Association (OIDA), replacement of one 60 Watt bulb with an equivalent lumens LED white light bulb will
- Save over 1800 pounds of coal.
- Reduce carbon dioxide emissions by 3000 pounds
- Reduce Sulphur dioxide emissions by 12 pounds
- Creates no mercury emissions
DOE estimates that Solid State Lighting could potentially reduce the US electricity used for illumination up to 50% by 2025.
    Alleviate the need of more than 40 power stations of 1000MW.

## Slide 11: Flicker

## Slide 12: Flicker in Lighting
Flicker, flutter, shimmer
  Repetitive change in magnitude over time, or modulation, of the luminous flux or luminance of a light source
  Light output modulation
Visible vs. invisible, sensation vs. perception
  Visible flicker = Light output modulation is sensed and perceived (<60Hz~90Hz)
  Invisible flicker = Light output modulation is sensed, but not perceived (>90Hz)
  Sensation: external conditions are detected and neurons respond
  Perception: the brain detects AND the mouth can report it sees

## Slide 13: Light source modulation
T12
60W A19
A19 CFL
A-lamp/G-lamp
R30/PAR30
R38/PAR38
Notes: 13

## Slide 14
Even battery powered flashlights can be programmed to flicker

## Slide 15: Eye Saccade
Eye in motion from (e.g. left to right) more sensitive to flicker
Experiment: CRT with flickering bar (vs.) constant illuminating bar
  Above what frequency is image same?
  Implication to LED tail-lights (worst case scenario here)
  Experiment designed by Jane Roberts and A. Wilkins, Univ. Essex, gives worst case upper bound of perceptible flicker

## Slide 19: Experimental Setup
Participants view flickering line in the dark and make eye saccade
Which do you see?
Roberts and A. Wilkins(2013), Lehman et al (2011)

## Slide 20
Roberts and A. Wilkins(2013),

## Slide 21
Roberts and A. Wilkins(2013),

## Slide 22
Stroboscopic Effect:
Flickering light on a moving object

## Slide 23: Lighting Research Center (ASSIST) at RPI (Bullough, Sweater Hickcox, Klein, Lok, Narendran)
What is max value of flicker that a viewer can detect stroboscopic effects?
% flicker < 0.16*(flicker_freq) – 5.6
Example: flicker_freq=120Hz
% flicker < (0.16)*120-5.6 = 13.6%
Where % flicker = (Max – Min)/(Max+Min)
Alliance for Solid-State Illumination Systems and Technologies (ASSIST). 2012. ASSIST recommends… Flicker Parameters for Reducing Stroboscopic Effects from Solid-state Lighting Systems. Vol. 11, Iss. 1, Troy, NY: LRC
www.lrc.rpi.edu/programs/solidstate/assist/recommends/flicker.asp

## Slide 24: Flicker: Potential Health Effects
Photosensitive epilepsy
  Short exposure to 3 – 70 Hz flicker (i.e., visible modulation) may cause seizures in sensitive people
  1 in ~20,000 people
Malaise: headache and eyestrain
  Slower onset to frequencies in range of 100-120Hz have been published
  Exact population frequency is not known (not everyone affected)
Source: http://apps1.eere.energy.gov/buildings/publications/pdfs/ssl/veitch_flicker_philly2010.pdf
Notes: The catastrophic outcome that can occur in response to flicker is exemplified by epilepsy.
24

## Slide 25
Compared conventional (“flickering”) lighting (100Hz) with high-frequency (“non-flickering”) lighting (>20kHz)
A double-masked study of headache and eye-strain
Seminal study by A. Wilkins (1989)

## Slide 26
Timers
measured hours lamp was turned on
Hidden in casing
Showed HF lights left on for longer
A. Wilkins (1989)

## Slide 27: Headaches and lighting: over twice the occurance of headaches when magnetic ballasts with 120Hz
0
20
40
60
80
weekly incidence
% sample (N=33)
1
2
0
20
40
60
80
% sample (N=91)
3
4
0
1
2
3
4
3
4
Conventional
fluorescent
lighting
Fluorescent
lighting with
electronic
high-frequency
ballast
A. Wilkins (1989)

## Slide 28: Risk Assessment
Figure 1 Risk Matrix by Hazard. Greater opacity corresponds to greater certainty
Table 2 Risk Levels
Risk Level | Color code
Low | 
Medium | 
Serious | 
High | 
G, Ryder, R. Altkorn, X. Chen, JA Veitch, M. Poplawski, Safety 2012, the 11th World Conference on Injury Prevention and Safety Promotion

## Slide 29: LED Drivers and Flicker
What makes LEDs different? Why the concern about flicker?
Notes: 29

## Slide 30: Methods of Driving LEDs – Basic Circuit
Basic Circuit Advantages
  Simple and low cost
Basic Circuit Disadvantages
  Lower efficiency due to resistor R
  Uneven light intensity due to Vf variations from temperature (+/- 20%)
  Reliability impacted by Vf variations due to temperature – higher temperature causes increase in current causing higher junction temperature of LED
Notes: 30

## Slide 31: 1 Strings of LEDs with 1 Source
Operate the source as a current source instead of voltage source and regulate string current
Regulating current = regulating luminous intensity (if temperature is constant)
Series combination of LEDs with a voltage source (left), with a current source (right)
Notes: 31

## Slide 32
Basic Concept for LEDs
Light Output (luminance) is roughly proportional to the LED current.

## Slide 33
LIGHT
LIGHT FIXTURE
STRINGS OF LEDS
LED DRIVER
AC-DC Converter
AC source
SOURCE
AC Powered LED Lighting System
LED Drivers and Flicker: The Concern?
AC-DC converters often have 120Hz harmonics (flicker) in their current. How much is acceptable? (120Hz = twice the line frequency, which would be 100Hz in Europe.)
AC LEDs: It is possible to eliminate AC-DC converter using a few special techniques: Reduce costs, eliminate capacitors, smaller size, increased lifetime. But this gives 100Hz/120Hz flicker.
Notes: 33

## Slide 34
AC LEDs
Luminous Flux
(periodic every 1/120 sec)
is proportional to LED current
1. Rectify AC and send to LED string
2. Directly power two LED strings with opposite Anode/Cathode connections
Luminous Flux
Or a capacitor
Notes: 34

## Slide 35
(c) Simulation of current through HB LEDs. Luminance is proportional to current, causing lamp to flicker at the AC mains line frequency
(shown periodic every 1/60 sec)
(a) Rectify AC and send to LED string
(b) Directly power two LED strings with opposite Anode/Cathode connections
Luminous Flux
Or a capacitor
Failures may cause 60 Hz flicker: Open circuit in rectifier or in LED string
Notes: 35

## Slide 36
Bulb
LED DRIVER
AC-DC Converter
AC source
SOURCE
What About Power Electronic Drivers?
Single Stage: Has Power Factor Correction (PFC) but produces high (up to 100%) flicker at twice line frequency
Two Stages: Has PFC and the ability to reduce the 120 Hz flicker
Notes: 36

## Slide 37: Typical Single-Stage LED driver
Source: EE Web.com (March 27, 2013 article)
Flyback converter is able to keep input current in phase with AC voltage for PFC
Output LED current has substantial flicker at 120 Hz (unless peripheral circuits added for cancellation- Fang(2013), Hu(2012) )

## Slide 38: Typical Single-Stage LED driver
AC source input current in phase with line voltage
Output LED current has large flicker at 120 Hz
Fang(2013), IEEE TPEL

## Slide 39: Typical Dual-Stage LED driver

## Slide 40: It is possible to eliminate flicker completely
DC/DC or AC/DC converter acts as pre-regulator to create Vo above the required highest string voltage (voltage imbalance among strings!)
Linear regulators can keep current constant and the same in each string
PWM dimming (series) can be added to the Linear current regulator
Adjust Vo according to Vmin so Vo adapts to which strings are on/off
Figure From: IEEE TRANSACTIONS ON POWER ELECTRONICS, NOVEMBER 2008
“LED Driver With Self-Adaptive Drive Voltage”, Yuequan Hu and Milan M. Jovanovi´c,

## Slide 41: Power Factor Correction (PFC) Architecture Trade-Off
Dual-stage PFC
  Near perfect PFC possible
  With proper control and component design, flicker can also be kept minimal
  BUT: Boost stage adds components and cost
Single-Stage with PFC
  Modulating the input impedance improves PF
  BUT: Higher %Flicker at twice line frequency usually remains
  (Some have proposed combining passive pfc with single stage power converter… to impact both pf and flicker. )
It Comes Down to Flicker vs. cost vs. Performance

## Slide 42: Triac Phase Modulate Dimmers
Notes: 42

## Slide 43: PWM Dimming
Common LED Currents
Driver
Vdimmer
(1/T=f=100~120Hz)
A few LED lamps will visually flicker on AC wall dimmers (3Hz~25Hz) because they fail to work properly.
Used with either AC Mains or DC power as source
Can increase or induce flicker
Notes: 43

## Slide 44: Triac Dimmer
Dimmer malfunctions during light load with current less than minimum latching and holding currents, as is often the case with single LED lamps (Rand et al, PESC 2007).
  Solution: Add resistor or active load to the LED lamp: When dimming on triac, there is a forced power sink wasting energy to keep the triac on. (not great…)
Require a large hold-up capacitor to keep current in LEDs during the off-time of the dimmer (not realistic in size, cost, lifespan, etc.)
Difficulties caused by phase modulated dimmers
Notes: 44

## Slide 45: The Concern?
A few LED lamps will visually flicker on AC wall dimmers (3Hz~25Hz) because they fail to work properly.
Commercial LED lamp flickers at 3.15Hz when connected to typical residential dimmer switch.
Notes: 45

## Slide 46: Solution: holdup capacitor – LM3445
Vcc receives power at all times
Triac off– the capacitive valley fill circuit still powers the buck converter’s input voltage
Dimming level corresponds to the on-time of the Triac
Add Passive PFC
Many LED driver manufacturers now keep DC voltage across LEDs at all times, even during triac off-time
Notes: 46

## Slide 47: LED PWM Dimming Example
~50% dimmer
~25% dimmer
~0% dimmer
Switch
100% dimmer
~75% dimmer

## Slide 48
      Various level of 120 Hz flicker appear in all lighting
      The driving method for LED lamps influences the amount and shape of the flicker
      IEEE PAR1789 Standard Committee intends to provide a recommended practice for how to apply this information
Conclusions
http://grouper.ieee.org/groups/1789/

## Slide 49: IEEE PAR 1789 - PURPOSE
There is a need to create a community where experts among the above different fields can communicate.
Suggest a recommended practice, not a standard. Representation on IEEE P1789 from ENERGY STAR, CIE and NEMA may later incorporate findings into standards if deemed necessary.
IEEE Standards Association has a unique open process that MUST involve all interest groups including academics, national labs, industry, customers… (current membership is ~50 with around 25% academics, 25% government labs, 50% industry/consulting)
International participation from members and from standards groups
Vision: Bring together a community of lighting environmental psychologists, medical researchers, lamp designers, LED driver designers, and LED lamp users to openly discuss concerns for LED lighting.
Notes: 49

## Slide 50: IEEE PAR 1789 - PURPOSE
Describe some possible health risks, such as headaches, eye strain and epileptic seizure, associated with low frequency modulation of High Brightness LEDs in different applications
Provide recommended practices to aid design of LED driving systems to modulate at safe frequencies for their particular applications in order to protect against the described health risks.
http://grouper.ieee.org/groups/1789/
Notes: 50